## Load Calc
Quickie Load Estimate Form
Project Name:
Rules of Thumb for Cooling Load Estimates |  |  |  |  | Table 1
Computer & Equipment Load
Room Design Conditions |  |  |  |  | Quantity | Model |  |  | BTU/Hr | Total BTU | BTU/Hr
| Temperature |  | 72F +/- 1F |  | 1 | Ricoh |  |  |  | 0 | Watts
| Humidity |  | 50% +/- 1% RH |  | 1 |  |  |  |  | 0 | KW
Sensible Heat Ratio
| Sensible Heat Gain |  | 0.90 to 0.95
Total Heat Gain
Load Density
| sq ft/Ton |  | 50 to 100
(Total heat gain / 12000)
Preferred Air Distribution
| Underfloor/overhead |  | Underfloor
Ventilation Rate
| CFM/person |  | 10-15 Maximum
Humidificaiton |  |  |  |  | Total BTU/HR |  |  |  |  | 0
| Lbs Moisture/100 CFM |  | 3 |  | NOTE: If BTU is not available, get total wattage input mult. X 3.4 = BTU/Hr
of outside air
Item |  |  |  |  | Quantity |  |  | Factor |  | BTU/HR | 95º F
[8 empty] | Outside Design Temp |  |  | 100º F
[8 empty] | 95º F |  |  | 105º F
1 | Windows Exposed to sun |  |  | South |  | sq ft | X | 70 | =
| (Use only one exposure: Select the one that gives the largest result) (If no venetian or shading device is available, mult. X 1.4) |  |  | East, West, Southeast |  | sq ft |  | 92
|  |  |  | Northwest |  | sq ft |  | 72
|  |  |  | Northeast |  | sq ft |  | 75
|  |  |  | North |  | sq ft |  | 10
2 | All windows not included in item 1 |  |  |  |  | sq ft | X | 26 | =
3 | Wall Exposed to sun |  |  | Light construction |  | linear ft | X | 75 | =
| (Use only the wall with the |  |  | Heavy construction |  | linear ft |  | 55
| exposure used in item 1) |  |  | (12" masonry or insulation)
4 | Shade walls not included in item 3 |  |  |  |  | linear ft | X | 40 | =
5 | Partitions | All interior walls adjacent to an unconditioned space |  |  |  | linear ft | X | 35 | =
6 | Ceiling or roof |  |  | Ceiling with unconditioned, |  | sq ft | X | 5 | =
occupied space above
|  | Ceiling w/attic above |  | No Insulation |  | sq ft |  | 12
|  |  |  | 2" or more insulation |  | sq ft |  | 5
|  | Flat roof w/ceiling below |  | No Insulation |  | sq ft |  | 10
|  |  |  | 2" or more insulation |  | sq ft |  | 5
7 | Floor | Over unconditioned space or vented crawlspace |  |  |  | sq ft | X | 5 | =
(Do not figure heat gain for floor directly on ground or over unheated basement)
8 | People |  |  | Number of people |  |  | X | 750 | =
(includes allowance for ventilation)
9 | Lights |  |  |  |  | Watts | X | 3.4 | = |  |  | Watts | 3.4
|  |  |  | (if not available, use 3 watts/sq ft of floor area) | [7 empty] | Sq ft | 10.2
10 | Computer Load Total BTU/Hr |  |  |  | From Table 1 |  |  | 0 | =
(if not available in BTU, mult total watts x 3.4)
[8 empty] | Total BTU Cooling Load: | 0
Note on I29: Click in this cell for a drop-down list
Note on J6: Click in this cell for a drop-down list of available units
Note on J9: Cells shaded this color allow data entry
Note on G52: Select Watts or Sq Ft